## Slide 1: High Power Efficiency Design Approach of a LLC Resonant Converter for UPS Battery Charger Application and Battery Charge-Discharge Regression Model
ICASEM 2020
Turhan Can KArgın

## Slide 2: Presentation Guides
Introduction
LLC Rezonant Converter
Circuit Design
Simulation Results
Regression Models with Machine Learning
Conclusion

## Slide 3: Introduction
This presentation present the analysis and design considerations for a half-bridge LLC resonant DC-DC converter. Using the fundamental approximation, the voltage and current waveforms are analyzed and the gain equations are obtained. Half-bridge LLC resonant converter has 400V input and 48V/3.1A output.The circuit is simulated using PSIM software. In addition, it is presented as secondary output to find the charge-discharge models under varying conditions by deriving the regression models with machine learning algorithms where the battery electricity energy consumption, battery status and temperature data can be analyzed.

## Slide 4: LLC Rezonant Converter
1. Hard Switching and Soft Switching?
2. The advantages of LLC Rezonant Converter
3. Why to use as UPS Battery Charger
Block diagram of a universal battery charger

## Slide 5: Circuit Design
  Define the system specifications and determine the maximum and minimum voltage gains of the resonant network
A schematic of half-bridge LLC resonant converter

## Slide 6: Circuit Design
  Calculate the Equivalent Load Resistance and Design the resonant network
Peak Gain (Attainable Maximum Gain) vs. Q for Different m Values
With m value chosen in previous slide, read proper Q value from the peak gain curves in Figure that allows enough peak gain. Considering the load transient and stable zero-voltages-witching (ZVS) operation, 10~20% margin should be introduced on the maximum gain when determining the peak gain.

## Slide 7: Circuit Design
  Design the transformer and select the resonant capacitor
Typical Gain Curves of LLC Resonant Converter
From the gain curve of Figure, the minimum switching frequency will be obtained

## Slide 8
Therotical calculation results
Design Specification
Define Ratio ‘n’
Select Value of k and Q
Define Value of Mmax-Mmin
Check M, k and Q Graph
Are the values of M, k and Q is in the Limit.(ZVS)
Calculate ‘Cr’
Calculate ‘Rac’
YES
NO
Design results are calculated as;
= %96= 363.276V k = 9.4
= 150 W = 400 V
= 148.8W = 1.1066
= 1.22
= 251.9 Ω = 19.03 nF
= 110 uH = 600 uH
= 57.78 uH = 2.879 uF
= 542.2177 uH= 36
= 8 = 1.044 A
= 495 V Q = 0.302
Circuit design results

## Slide 9: Simulation Results

## Slide 10: Simulation Results
Output Voltage (V) and output current (A) of the LLC Resonant Converter

## Slide 11
= %9
MOSFET voltage (V) and current (A) achieving soft switching

## Slide 12
Typical Voltage (V) and current (A) waveforms of half-bridge LLC resonant converter
Simulation Voltage (V) and current (A) waveforms of resonant converter

## Slide 13: Regression Models with Machine Learning
Results Regression Models | Root Mean Square Error | Score
SVR | 1057.0299 | 0.0008
Linear Regression | 77.2032 | 0.9946
LGBM Regressor | 465.0893 | 0.8065
XGB Regressor | 93.0894 | 0.9922
Gradient Boosting Regressor | 70.8098 | 0.9955
Random Forest Regressor | 67.843 | 0.9959
Decision Tree Regressor | 128.161 | 0.9853
MLP Regressor | 994.0306 | 0.1164
K-Neighbours Regressor | 104.8204 | 0.9901
Results Regression Models | Root Mean Square Error | 
SVR | 1057.0299 | 0.0008
Linear Regression | 77.2032 | 0.9946
LGBM Regressor | 465.0893 | 0.8065
XGB Regressor | 93.0894 | 0.9922
Gradient Boosting Regressor | 70.8098 | 0.9955
Random Forest Regressor | 67.843 | 0.9959
Decision Tree Regressor | 128.161 | 0.9853
MLP Regressor | 994.0306 | 0.1164
K-Neighbours Regressor | 104.8204 | 0.9901
Regression model comparison using Python

## Slide 14: Regression Models with Machine Learning
Visualization of battery discharge regression models

## Slide 15: Conclusion
Designing circuit by using PCB design program (Eagle), production and testing of the circuit. Also,comparison with practical, theoretical and simulation results will be done soon.
Creating a database with the obtained data and creating a battery charge-discharge regression model were done.
Simulation of the system with the simulation program (PSIM) and comparison with the theoretical results were done.
Circuit analysing and therotical calculations were made.

## Slide 16: Thank You